Investigative Report

On-site State Investigation

Facility Address: 12844 MILITARY RD S. TUKWILA, WA 98168-3045

Laboratory Director: N/A

CLIA Number: N/A

Credential Number: RTF.FS.61487645

Medicare Number: N/A

Shell Number: N/A

Date(s) of Investigation: 03/06/2026-

State Licensing Priority: B

Federal Certification Priority: N/A

Intake Details: (List of concerns reported in the original complaint.)

The Department of Health (DOH) received a complaint that alleged that there has been a known, prolonged exposure, of contaminated water involving Legionella species, Legionella pneumophila, at the respondent facility.

Allegation(s): (The allegation(s) listed below is what the department has jurisdiction and authorization to investigate. An allegation is considered an assertion of improper practice or condition that could result in a violation of facility law or rule.)

- Allegation: Potential violation of WAC 246-337-045, Governance and administration, by having failed to provide organizational guidance and oversight to ensure that resources support and staff provides safe and adequate resident care. (1)(a)(iii) A policy addressing the provision of sufficient resources such as personnel, facilities, equipment, and supplies to meet the needs of the population served. (1)(d)(iii) Complied with by staff.

- Allegation: Potential violation of WAC 246-337-048, Quality improvement program, by having failed to ensure ongoing maintenance of a coordinated quality improvement program to improve the quality of care provided to residents and to identify and prevent serious or unanticipated resident and facility outcomes. (2)(e) Injuries which result in serious or unanticipated outcomes. (3) Review serious or unanticipated resident or facility outcomes in a timely manner. (4) Implement and document changes or improvements made to prevent future occurrences of any serious or unanticipated resident outcome.

- Allegation: Potential violation of WAC 246-337-060, Infection control, by having failed to implement and maintain an infection control program that prevents the transmission of infections and communicable disease among residents, staff, and visitors. (1)(g) Environmental management. (3) Providing all necessary supplies and equipment to implement the infection control program.

- Allegation: Potential violation of WAC 246-337-065, Safety and security, by having failed to protect resident safety and security by developing written policies and procedures. (5)(d) Injuries resulting in an inpatient hospital stay. (5)(e) Disruption of services through internal or external emergency or disaster.

- Allegation: Potential violation of WAC 246-337-075, Resident rights, by having failed to establish a process to ensure resident rights are protected. (2)(g) Have a safe and clean environment.

- Allegation: Potential violation of WAC 246-337-080, Resident care services, by having failed to establish and implement policies and procedures that describe how the licensee meets the residents' health care needs. (2)(h)(ii) Observing residents for signs and symptoms of illness or trauma. (2)(h)(iii) Reporting abnormal signs and symptoms according to an established protocol.

Investigative Process Included: (This is what the Investigator did in terms of methods employed to conduct inquiry.)

Pre-investigation Activity:

- The Investigator reviewed relevant Washington Administrative Codes (WACs) and Revised Code of Washington (RCWs) statutes and regulations.

- The Investigator reviewed the complaint allegations.

- The Investigator developed an investigation plan;

  - Coordinate with sister agencies,

  - Request policies and procedures,

  - Request documentation related to water treatment, temperature togs, and other documentation related to the care of water in the facility,

  - Request up to date documentation showing what has been done at the facility to account for a history of legionella.

Investigation Activity:

Observations

- The Investigator conducted an on-sight review with Staff A, the interim Chief Operating Officer, and Staff B, the Facility Manager,

- The onsite consisted of a facility tour, observation of the holding tanks, piping system, staff and patient access points, allocation of bottled water, and general observation of facility safety and security.

Interviews

- The Investigator conducted an interview with Staff C, Nurse Manager

- The Investigator conducted an interview with Staff B,  Facility Manager

Document Review

- The Investigator reviewed policies and procedures

- The Investigator reviewed the Water Management Plan

- The Investigator reviewed facility Risk Hazard Analysis documentation

- The Investigator reviewed Ice Machine inspection reports

- The Investigator reviewed Garrett Callahan Legionella test results

Summary of Findings (Narrative overview of the results of investigation.)

The DOH received a complaint that alleged that there has been a known, prolonged exposure, of contaminated water involving Legionella species, Legionella pneumophila, at the respondent facility.

The Investigator conducted an unannounced onsite visit of the facility on 03/06/26 at (time). During an on-site tour conducted by the Investigator on 03/06/2026 starting at approximately 09:16 AM, the Investigator performed a physical walk-through of the facility and assessed the environment of care and inspected the water infrastructure. The Investigator observed that the building's footprint reflected several expansion phases from 1975 to 2014, contributing to the complexity of the current plumbing system. The Investigator observed that three units were currently occupied while two remained vacant, which were slated for rental by the Healthcare Authority once construction was complete. During the inspection of mechanical and support spaces, the Investigator observed maintenance staff actively working on piping in sections Q2 and Q4.

During the onsite on 03/06/26, the Investigator inquired with staff B about the facility's water supply and verified that water is supplied via a single meter for the west building and a dedicated chlorine injection pump located in the penthouse for the south building. The Investigator noted that chlorine is injected into the main line under the pumps and that the facility’s air conditioning "Chiller" unit is serviced monthly by a local service provider. To prevent the creation of dead legs or areas of pipe where water would remain without flowing, the Investigator observed that the facility pool had been capped and disconnected, with the space now used for stowage. The Investigator inquired about the boiler system and was informed that legacy units reaching only 130°F were replaced in late 2025 with a new system featuring 200–300 gallon capacity tanks capable of reaching 170°F. The Investigator further noted that staff member B coordinated a monthly "hyper-heat" cycle by bypassing mixing valves to push high-temperature water through the system.

During the tour on 03/0626,, the Investigator observed distal-end filters installed on sinks and showers in patient rooms and on all medication prep sinks, although they were secured behind panels accessible only to maintenance staff. The Investigator identified a significant gap in the kitchen and scullery areas where no filters were installed despite active food handling. The Investigator further found that the ice machine was out of commission following a positive Legionella test result. While "Do Not Drink" signs were present at patient sinks, the Investigator discovered that no such warnings were in the shower stalls. The Investigator noted that patients were provided with bottled water in dining spaces and must go to the nursing desk or medication room for additional water needs. The Investigator observed that most showers lack hoses, with only two hand units identified in the facility.

The Investigator collected water quality data on site that showed a temperature of 164°F in the Scullery, while residential units showed significant fluctuations in chlorine levels. Specifically, the Investigator measured 118°F with a chlorine level of 0.21 ppm in the 1 North unit, 116°F with 1.21 ppm in 2 North, and 106°F with 1.65 ppm at Distal Site 1 West. The Investigator was informed that on-site laundry is suspended, laundry is cleaned professionally off site, and a full facility re-pipe is planned for 2027–2028 to address failing galvanized and copper lines.

In an interview conducted by Investigator 1 on 03/06/2026 at approximately 11:29 AM with Staff C, the Nurse Manager, the Investigator inquired about the medication administration process and the use of the facility's water supply. Staff C stated that for the current census of 27–28 patients, medications are administered exclusively with bottled water, Pedialyte, or Gatorade. Staff C noted that the facility  relied on bottled water for "over a year," a practice that began shortly after their hire in 2024. The Investigator inquired about communication regarding water safety, and Staff C stated that information is shared with staff and patients through daily "huddles," inter-shift meetings, emails, and physical signage. Staff C further noted that there is a "daily awareness" among staff regarding resident concerns about their health in relation to the water supply.

In an interview conducted by Investigator 1 on 03/06/2026 at approximately 12:11 PM with Staff B, the Facility Manager, the Investigator inquired about the facility's water management plan and current mitigation efforts. Staff B stated the plan is maintained in partnership with Garrett-Callahan and that water testing was increased to 25 samples per month starting in October 2024. Staff B noted that chlorine levels are targeted at 3 ppm and that Nephros distal-end filters have been installed in designated sinks and showers, although they noted these filters occasionally face shipping delays. The Investigator inquired about the flushing protocols, and Staff B stated that the facility currently utilizes six staff members to perform ten-minute flushes of all end-use points every hour to prevent water stagnation due to the low patient census. Staff B also noted the use of a monthly "hyper-heating" procedure to address Legionella in the piping "biofilm" and confirmed that bottled water continues to be provided for all consumption.

The Investigator reviewed WAC 246-215, the Washington State Food Code, which sets the safety standards for food service operations. The Investigator noted that WAC 246-215-05115 required water used in food establishments to meet the drinking water quality standards of WAC 246-290. The Investigator further noted that WAC 246-215-05240 requires water treatment devices like point-of-use filters to be maintained according to manufacturer instructions.

The Investigator reviewed WAC 246-290, which governs public water systems. The Investigator noted that WAC 246-290-601 specifically identifies Legionella as a microbial contaminant that requires filtration and disinfection. The Investigator found that these regulations, combined with Department of Health safety guidance, require facilities to flush and sanitize all equipment connected to the water supply and replace associated water filters when contamination is found.

The Investigator reviewed a document titled “OHBH Water Management Program,” which established a multidisciplinary Water Management Team (WMT) responsible for overseeing water safety, including the CEO, COO, Facilities Manager, and Infection Control Nurse. The WMP outlines a formal protocol for monthly Legionella testing via a third-party laboratory, with results typically reviewed within 10 working days. The document showed that the plan sets specific water temperature control limits between 105°F and 120°F for resident fixtures and identifies a chlorine control limit of 0.3 ppm to 0.5 ppm. Documentation within the plan described preventative maintenance including monthly fixture flushing and a monthly "hyper-heating" of the hot water system to 170°F. The document further showed that the WMT is tasked with determining the necessity of "Boiling Mandates" and notified staff of internal water emergencies. However, the document showed that the plan does not explicitly detail protocols for resident notification or the use of bottled water as a remediation strategy. Additionally, the WMP lacks specific, mandatory disinfection steps following a positive Legionella result, stating instead that the "WMT will determine how to proceed" based on individual sample results.

The Investigator reviewed the document titled “Garratt Callahan Water Management Plan,” a technical document providing a "Risk Assessment and Management Strategy" for the facility’s water systems. The document showed that the plan utilizes a "Confirmation" protocol that relies on routine Legionella testing (DWR5S) and the monitoring of hospital-acquired disease cases as primary validation methods. The document includes a detailed response flowchart for Legionella detection, which directs staff to specific remediation actions based on the severity of the test results. While the plan is forward-looking for the 2025-2026 period, the document showed "Team Member Notes" from 2024, indicating that the facility was actively revising its management strategy during that time. However, the document did not contain a historical log of past detections, focusing instead on the procedural requirements for responding to future disease risks.

The Investigator reviewed a document titled “Corrective Action Plans,” which provide a chronological log of Legionella detections and remediation efforts from early 2023 through April 2025. The document showed that positive Legionella tests were recorded in February 2023, followed by a series of recurring positives in late 2024 and nearly every month of early 2025 (January, February, March, and April). In response to these triggers, the facility documented multiple remediation steps, including the "HydroTreat Process" (April 2023) involving chemical injections, and the installation of chlorine injectors and shower filters. The document showed that the facility also implemented extensive flushing protocols, including all-day flushing events and high-temperature flushes (162°F to 180°F). While follow-up testing in 2023 initially showed "0 positive results," the document showed that the recurring positives in 2024 and 2025 led to a documented increase in the frequency and intensity of these flushing and chemical treatment protocols.

The Investigator reviewed laboratory results and service invoices from an ice machine service company, regarding the facility’s ice machine located in the NB09 kitchen area. The Investigator noted that a water sample collected on 02/12/2026 from the "NB09 Ice Machine" tested positive for Legionella pneumophila Serogroup 2-15 at a concentration of 0.4 CFU/mL. A subsequent retest of the ice on 02/26/2026 confirmed the continued presence of the pathogen, identifying Legionella pneumophila Serogroup 1 at a concentration of 0.4 CFU/mL.

The Investigator reviewed service invoices indicating that the facility attempted professional remediation three times during this period. An invoice dated 01/14/2026 showed that two machines were cleaned and sanitized, and a water filter was replaced. The service invoices showed that following the February positive results, a second service on 02/25/2026 involved deep cleaning, sanitizing, and wiping all internal parts with bleach. A final invoice dated 03/12/2026 indicated that the kitchen ice machine was again disassembled, scrubbed, and sanitized, and the water filters were replaced and flushed. The Investigator verified during the on-site tour on 03/06/2026 that the machine remained out of commission due to the persistent Legionella contamination.

Based on visual investigation, interview, invoice/laboratory review, and documentation review, the Investigator determined that the facility maintained patient safety and remained in compliance with state regulations during an environmental exposure to Legionella. However, the findings do substantiate specific, isolated failures requiring corrective action; The facility failed to install and maintain adequate filtration on its ice machines and kitchen water systems, representing a gap in comprehensive environmental infection control. The facility failed to post proper, visible signage in the patient showers to adequately inform patients of the current water status and safety procedures. The current mitigation strategies, such as the allocation of bottled water, are insufficient for long-term safety and emergency resolution. While the facility's immediate mitigation efforts successfully protected resident health, a sustainable and permanent infrastructure solution is required.

Conclusion/ Results of Investigation

- Allegation: The Investigator found the facility in compliance with WAC 246-337-045, Governance and administration.

- Allegation: The Investigator found the facility in compliance with WAC 246-337-048, Quality improvement program.

- Allegation: The Investigator found the facility not in compliance with WAC 246-337-060, Infection control.

- Allegation: The Investigator found the facility not in compliance with WAC 246-337-065, Safety and security.

- Allegation: The Investigator found the facility not in compliance with WAC 246-337-075, Resident rights.

- Allegation: The Investigator found the facility in compliance with WAC 246-337-080, Resident care services.

Actions:

Statement of Deficiency, Plan of Correction Reviewed

No Additional Referrals Needed